Fire Hydrants Requirements

- All Fire Protection water supplies will comply with the 2006 International Fire Code, Section 508.

  - Section 508.5.1 No facility or building will be more than 400 feet from a fire hydrant on an approved fire apparatus access road.

    - R-3 & U occupancies, the distance shall be 600 feet.

    - For fully sprinklered buildings, the distance shall be 600 feet.

- Hydrants will be Muller Centurion, red in color.

- Fire Hydrants will have two (2) 2 ½-inch outlets and one 5” inch pumper outlet.  All 2 ½-inch outlets will be National Standard thread.  The 5” inch pumper outlet will have 5-inch Storz fittings with storz cap & chain.  Outlets will be in compliance with NFPA 1963.

- Hydrants will be compliant with AWWA Standard C502, the latest revisions thereof.  Hydrants will be painted red. The hydrant will have a positive and automatic barrel drain and will be of the safety or breakaway style.  Fire Hydrants will have a 5 ¼” inlet to maximize water flow.

- Where needed, Mulvane Fire Department may require hydrants to be protected by two or more posts, each 4” in diameter by 3 feet in height. Vehicle Impact Protection must meet requirements of 2006 IFC Section 508.5.6 & Section 312.

- Fire hydrants must be installed, tested, and accepted prior to the issuance of a building permit and/or occupancy permit. 2006 IFC Section 508.4

Capt. Lowell L. Ester

Fire Inspector II

www.mulvaneemergencyservices.org

Created: August 2004

Revised: September 2010